## Cover & Basis
F&K Estimatings
Electrical Takeoff Sample — Cover & Basis
Sample deliverable — prepared on a representative project to show format and level of detail. Not a client project. Quantities are computed from the sample project dimensions stated below; unit costs are illustrative (pricing basis: September 2026, national average, not a quote).
Project | Representative sample project: 6,000 SF office tenant fit-out in a 100' x 60' single-story building
Trade / CSI | Electrical — CSI Division 26
Description | Tenant electrical for a 6,000 SF office: 208Y/120 V 3-phase, 4-wire. A 400 A tenant main panel (MDP) feeds two 7.5-ton rooftop units, an electric water heater and a 225 A lighting/receptacle panel (LP-1). Both panels sit in Electrical/IT room 109. Branch circuits run in 3/4" EMT above a 9'-0" ACT ceiling (raceway elevation 10'-0"); every conduit length in the circuit schedule is measured from the panel to the served area on the sample plan, so each run can be traced.
Prepared by | F&K Estimatings (fandkestimatings.us) — sample for format illustration only
ASSUMPTIONS & BASIS — blue values are inputs; change one and the workbook recalculates
Section | Parameter | Name used in formulas | Value | Unit | Note / basis
Building | Tenant area | gross_sf | 6000 | SF | 100' x 60'
Raceway | Panel location, x (east of SW corner) | panel_x | 68 | ft | Electrical/IT 109
Raceway | Panel location, y (north of SW corner) | panel_y | 6 | ft
Raceway | Panel top to ceiling raceway | panel_rise | 4 | ft | Panel top 6'-0" to 10'-0"
Raceway | Conduit between lighting j-boxes | lt_sp | 10 | ft | 8' x 10' fixture grid
Raceway | Horizontal run between receptacles | rc_sp | 12 | ft
Raceway | Drop to receptacle (10'-0" to 18" AFF) | rc_drop | 8.5 | ft
Raceway | Extra horizontal to a dedicated outlet | dd_run | 10 | ft
Raceway | Run per exhaust fan | ef_run | 8 | ft
Raceway | Ceiling to rooftop disconnect | rtu_rise | 10 | ft | Roof 16'-0" + 4' to disconnect
Raceway | Drop to water heater disconnect | wh_drop | 6 | ft
Wire | Wire make-up per conductor per box/termination | makeup_ft | 1 | ft
Wire | Upsize #12 to #10 when circuit conduit length exceeds | vd_lf | 100 | ft | Voltage-drop rule of thumb for 120 V 20 A; ground upsized with phase
Feeder | MDP to LP-1 feeder length | fdr_len | 15 | ft | Same room
Feeder | Feeder make-up per conductor per end | fdr_term | 3 | ft
Fixtures | Open office area | oo_area | 3588 | SF | L-shaped area south of y=45'
Fixtures | Area per Type A troffer, open office | sf_a_open | 80 | SF
Fixtures | Area per Type A troffer, enclosed rooms | sf_a_room | 60 | SF
Fixtures | Private offices (12' x 15') | n_off | 5 | EA
Fixtures | Type A 2x4 LED troffer 40 W | fx_a | 73 | EA | Open office + offices + conference + break
Fixtures | Type B 6" LED downlight 15 W (lobby) | fx_b | 8 | EA | 1 per 40 SF
Fixtures | Type C 2x2 LED flat panel 30 W (restrooms) | fx_c | 4 | EA | 1 per 66 SF
Fixtures | Type D 4' LED strip 40 W (elec + janitor) | fx_d | 3 | EA | 2 + 1
Fixtures | Type X exit / emergency combo | fx_x | 6 | EA | Sample sheet E-101
Devices | Duplex receptacles 20 A (general) | n_dup | 54 | EA | Open office 24, offices 4 ea, conference 4, lobby 4, elec 2
Devices | GFCI receptacles 20 A | n_gfci | 9 | EA | Break counter 6, restrooms 2, janitor 1
Devices | Dedicated receptacles 20 A | n_ded | 4 | EA | Refrigerator, microwave, IT rack, copier
Devices | Wall-box occupancy sensors | n_occw | 10 | EA | Offices, conference, break, restrooms, janitor
Devices | Ceiling occupancy sensors + power packs (open office) | n_occc | 6 | EA
Devices | Toggle switches | n_sw | 2 | EA | Lobby, electrical room
Rates | Electrician labor rate (burdened, blended) | rate_elec | 82 | $/hr | Illustrative
Markups | Sales tax on material | tax_rate | 7% | % | Assumption
Markups | Overhead | oh_pct | 10% | % | Assumption
Markups | Profit | profit_pct | 10% | % | Assumption
SCOPE INCLUDED
• Tenant main panel MDP, panel LP-1 and feeder
• Branch circuits: EMT, THHN wire, boxes, fittings
• Wiring devices, occupancy sensors, light fixtures Types A-X
• RTU and water heater circuits with disconnects
• Testing and labeling
EXCLUSIONS / BY OTHERS
• Utility service and service-entrance conductors to MDP (by shell)
• Fire alarm, data/telecom cabling, security
• Furniture power feeds / power poles (by furniture vendor)
• Roof penetrations and patching
• Permit fees; engineered load calculation and voltage-drop study
SAMPLE DRAWING LIST (sheets of the representative sample project, not a real plan set)
• E-001 — Legend, fixture schedule, notes (sample)
• E-101 — Lighting plan (sample)
• E-201 — Power plan (sample)
• E-301 — Panel schedules MDP / LP-1, one-line (sample)

## Circuit Schedule
F&K Estimatings
Electrical Takeoff Sample — Panel & circuit schedule (conduit and wire measured per circuit)
Sample deliverable — prepared on a representative project to show format and level of detail. Not a client project. Quantities are computed from the sample project dimensions stated below; unit costs are illustrative (pricing basis: September 2026, national average, not a quote).
Home run = Manhattan distance from the panel to the served area + panel rise. Branch = devices x LF per device. One circuit per home-run conduit (no shared neutrals) - conservative. Load VA is illustrative nameplate/180 VA-per-yoke, not an engineered load calculation.
Circuit | Panel | Description | Type | Area x (ft) | Area y (ft) | Devices / fixtures | LF per device | Home run LF | Branch LF | Conduit LF | Conduit | Wire (base) | Wire (if long) | Phase + neutral cond. | Wire used | Phase/neutral wire LF | Ground (base) | Ground (if long) | Ground used | Ground wire LF | Load VA | Poles | Breaker A
LP1-1 | LP-1 | Lighting - open office west (Type A) | L | 16 | 22 | 23 | 10 | 72 | 230 | 302 | 3/4 in | #12 | #10 | 2 | #10 | 652 | #12 | #10 | #10 | 326 | 920 | 1 | 20
LP1-3 | LP-1 | Lighting - open office east (Type A) | L | 46 | 22 | 22 | 10 | 42 | 220 | 262 | 3/4 in | #12 | #10 | 2 | #10 | 570 | #12 | #10 | #10 | 285 | 880 | 1 | 20
LP1-5 | LP-1 | Lighting - offices 101-105 + conference (Type A) | L | 40 | 52.5 | 20 | 10 | 78.5 | 200 | 278.5 | 3/4 in | #12 | #10 | 2 | #10 | 599 | #12 | #10 | #10 | 299.5 | 800 | 1 | 20
LP1-7 | LP-1 | Lighting - break room (A) + lobby (B) | L | 88 | 38 | 16 | 10 | 56 | 160 | 216 | 3/4 in | #12 | #10 | 2 | #10 | 466 | #12 | #10 | #10 | 233 | 440 | 1 | 20
LP1-9 | LP-1 | Lighting - restrooms (C), support (D), exit/emergency (X) | L | 70 | 20 | 13 | 10 | 20 | 130 | 150 | 3/4 in | #12 | #10 | 2 | #10 | 328 | #12 | #10 | #10 | 164 | 270 | 1 | 20
LP1-2 | LP-1 | Receptacles - open office SW | R | 10 | 12 | 6 | 20.5 | 68 | 123 | 191 | 3/4 in | #12 | #10 | 2 | #10 | 396 | #12 | #10 | #10 | 198 | 1080 | 1 | 20
LP1-4 | LP-1 | Receptacles - open office NW | R | 10 | 33 | 6 | 20.5 | 89 | 123 | 212 | 3/4 in | #12 | #10 | 2 | #10 | 438 | #12 | #10 | #10 | 219 | 1080 | 1 | 20
LP1-6 | LP-1 | Receptacles - open office SE | R | 40 | 12 | 6 | 20.5 | 38 | 123 | 161 | 3/4 in | #12 | #10 | 2 | #10 | 336 | #12 | #10 | #10 | 168 | 1080 | 1 | 20
LP1-8 | LP-1 | Receptacles - open office NE | R | 40 | 33 | 6 | 20.5 | 59 | 123 | 182 | 3/4 in | #12 | #10 | 2 | #10 | 378 | #12 | #10 | #10 | 189 | 1080 | 1 | 20
LP1-10 | LP-1 | Receptacles - offices 101-102 | R | 12 | 52.5 | 8 | 20.5 | 106.5 | 164 | 270.5 | 3/4 in | #12 | #10 | 2 | #10 | 559 | #12 | #10 | #10 | 279.5 | 1440 | 1 | 20
LP1-12 | LP-1 | Receptacles - offices 103-104 | R | 36 | 52.5 | 8 | 20.5 | 82.5 | 164 | 246.5 | 3/4 in | #12 | #10 | 2 | #10 | 511 | #12 | #10 | #10 | 255.5 | 1440 | 1 | 20
LP1-14 | LP-1 | Receptacles - office 105 + conference | R | 64 | 52.5 | 8 | 20.5 | 54.5 | 164 | 218.5 | 3/4 in | #12 | #10 | 2 | #10 | 455 | #12 | #10 | #10 | 227.5 | 1440 | 1 | 20
LP1-16 | LP-1 | Receptacles - lobby | R | 90 | 52.5 | 4 | 20.5 | 72.5 | 82 | 154.5 | 3/4 in | #12 | #10 | 2 | #10 | 319 | #12 | #10 | #10 | 159.5 | 720 | 1 | 20
LP1-18 | LP-1 | Receptacles - break counter GFCI (1) | R | 84 | 13 | 3 | 20.5 | 27 | 61.5 | 88.5 | 3/4 in | #12 | #10 | 2 | #12 | 185 | #12 | #10 | #12 | 92.5 | 540 | 1 | 20
LP1-20 | LP-1 | Receptacles - break counter GFCI (2) | R | 96 | 13 | 3 | 20.5 | 39 | 61.5 | 100.5 | 3/4 in | #12 | #10 | 2 | #10 | 209 | #12 | #10 | #10 | 104.5 | 540 | 1 | 20
LP1-22 | LP-1 | Dedicated - refrigerator | R | 78 | 20 | 1 | 18.5 | 28 | 18.5 | 46.5 | 3/4 in | #12 | #10 | 2 | #12 | 97 | #12 | #10 | #12 | 48.5 | 800 | 1 | 20
LP1-24 | LP-1 | Dedicated - microwave | R | 80 | 13 | 1 | 18.5 | 23 | 18.5 | 41.5 | 3/4 in | #12 | #10 | 2 | #12 | 87 | #12 | #10 | #12 | 43.5 | 1500 | 1 | 20
LP1-26 | LP-1 | Receptacles - restrooms + janitor GFCI | R | 86 | 6 | 3 | 20.5 | 22 | 61.5 | 83.5 | 3/4 in | #12 | #10 | 2 | #12 | 175 | #12 | #10 | #12 | 87.5 | 540 | 1 | 20
LP1-28 | LP-1 | Receptacles - electrical / IT room | R | 68 | 6 | 2 | 20.5 | 4 | 41 | 45 | 3/4 in | #12 | #10 | 2 | #12 | 96 | #12 | #10 | #12 | 48 | 360 | 1 | 20
LP1-30 | LP-1 | Dedicated - IT rack | R | 70 | 10 | 1 | 18.5 | 10 | 18.5 | 28.5 | 3/4 in | #12 | #10 | 2 | #12 | 61 | #12 | #10 | #12 | 30.5 | 1920 | 1 | 20
LP1-32 | LP-1 | Dedicated - copier | R | 60 | 40 | 1 | 18.5 | 46 | 18.5 | 64.5 | 3/4 in | #12 | #10 | 2 | #12 | 133 | #12 | #10 | #12 | 66.5 | 1500 | 1 | 20
LP1-11 | LP-1 | Exhaust fans EF-1, EF-2 (restrooms) | M | 86 | 6 | 2 | 8 | 22 | 16 | 38 | 3/4 in | #12 | #10 | 2 | #12 | 82 | #12 | #10 | #12 | 41 | 200 | 1 | 20
MDP-1 | MDP | RTU-1 7.5 ton (roof), 3-ph | E | 30 | 30 | 1 | 10 | 66 | 10 | 76 | 1 in | #8 | #8 | 3 | #8 | 234 | #10 | #10 | #10 | 78 | 13700 | 3 | 50
MDP-4 | MDP | RTU-2 7.5 ton (roof), 3-ph | E | 80 | 30 | 1 | 10 | 40 | 10 | 50 | 1 in | #8 | #8 | 3 | #8 | 156 | #10 | #10 | #10 | 52 | 13700 | 3 | 50
MDP-7 | MDP | WH-1 electric water heater 4.5 kW, 208 V 1-ph | E | 73 | 10 | 1 | 6 | 13 | 6 | 19 | 3/4 in | #10 | #10 | 2 | #10 | 42 | #10 | #10 | #10 | 21 | 4500 | 2 | 30
Totals | [5 empty] | 166 |  | 1178.5 | 2347.5 | 3526 | [5 empty] | 7564 |  |  |  | 3717 | 52470

## Quantity Takeoff
F&K Estimatings
Electrical Takeoff Sample — Quantity Takeoff
Sample deliverable — prepared on a representative project to show format and level of detail. Not a client project. Quantities are computed from the sample project dimensions stated below; unit costs are illustrative (pricing basis: September 2026, national average, not a quote).
Qty column holds live formulas that reference the named assumptions on 'Cover & Basis' (and the schedule sheets). Column I shows the same formula in readable form.
Item | CSI | Group | Description | Qty | Unit | Waste % | Qty incl. waste | Formula / basis | Notes
1 | 26 24 16 | Distribution | Panelboard MDP 400 A MCB, 208Y/120 V 3-ph 4-W, 30 ckt (incl. breakers) | 1 | EA | 0% | 1 | 1 (counted / stated)
2 | 26 24 16 | Distribution | Panelboard LP-1 225 A MLO, 42 ckt (incl. branch breakers) | 1 | EA | 0% | 1 | 1 (counted / stated)
3 | 26 05 33 | Distribution | Feeder MDP to LP-1: 2-1/2" EMT | 15 | LF | 5% | 15.75 | fdr_len
4 | 26 05 19 | Distribution | Feeder: 4 x 4/0 THHN Cu (3 phase + full neutral) | 84 | LF | 10% | 92.4 | 4 × (fdr_len+2 × fdr_term) | 225 A at 75 C
5 | 26 05 19 | Distribution | Feeder: 1 x #4 THHN Cu equipment ground | 21 | LF | 10% | 23.1 | fdr_len+2 × fdr_term
6 | 26 28 16 | Distribution | Disconnect 60 A 3-pole NEMA 3R (RTUs) | 2 | EA | 0% | 2 | 2 (counted / stated)
7 | 26 28 16 | Distribution | Disconnect 30 A 2-pole (WH-1) | 1 | EA | 0% | 1 | 1 (counted / stated)
8 | 26 24 16 | Distribution | Connected load on LP-1 (check) | 20570 | VA | 0% | 20570 | Σ[Circuit Schedule: Load VA where Panel = "LP-1"]
9 | 26 24 16 | Distribution | Connected load on MDP branch equipment (check) | 31900 | VA | 0% | 31900 | Σ[Circuit Schedule: Load VA where Panel = "MDP"]
10 | 26 05 33 | Raceway | EMT 3/4" (branch circuits) | 3400 | LF | 5% | 3570 | Σ[Circuit Schedule: Conduit LF where Conduit = "3/4 in"]
11 | 26 05 33 | Raceway | EMT 1" (RTU circuits) | 126 | LF | 5% | 132.3 | Σ[Circuit Schedule: Conduit LF where Conduit = "1 in"]
12 | 26 05 33 | Raceway | EMT couplings (1 per 10' stick) | 371 | EA | 0% | 371 | ROUNDUP((emt_34_w+emt_1_w)/10,0) | Labor carried in conduit unit
13 | 26 05 33 | Raceway | EMT straps (1 per 8') | 463 | EA | 0% | 463 | ROUNDUP((emt_34_w+emt_1_w)/8,0)
14 | 26 05 33 | Raceway | Device boxes 4" sq. w/ mud ring | 79 | EA | 0% | 79 | n_dup+n_gfci+n_ded+n_occw+n_sw
15 | 26 05 33 | Raceway | Lighting j-boxes above ceiling (1 per fixture) | 94 | EA | 0% | 94 | fx_a+fx_b+fx_c+fx_d+fx_x
16 | 26 05 33 | Raceway | EMT connectors (2 per box) | 346 | EA | 0% | 346 | 2 × (dev_boxes+j_boxes)
17 | 26 05 19 | Wire | THHN Cu #12 (phase, neutral and ground) | 1374 | LF | 10% | 1511.4 | Σ[Circuit Schedule: Phase/neutral wire LF where Wire used = "#12"]+Σ[Circuit Schedule: Ground wire LF where Ground used = "#12"] | Sum of phase/neutral + ground columns for this gauge
18 | 26 05 19 | Wire | THHN Cu #10 (phase, neutral and ground) | 9517 | LF | 10% | 10468.7 | Σ[Circuit Schedule: Phase/neutral wire LF where Wire used = "#10"]+Σ[Circuit Schedule: Ground wire LF where Ground used = "#10"] | Sum of phase/neutral + ground columns for this gauge
19 | 26 05 19 | Wire | THHN Cu #8 (phase, neutral and ground) | 390 | LF | 10% | 429 | Σ[Circuit Schedule: Phase/neutral wire LF where Wire used = "#8"]+Σ[Circuit Schedule: Ground wire LF where Ground used = "#8"] | Sum of phase/neutral + ground columns for this gauge
20 | 26 05 19 | Wire | MC fixture whips 6' (3-wire #12) | 94 | EA | 0% | 94 | fx_a+fx_b+fx_c+fx_d+fx_x
21 | 26 27 26 | Wiring devices | Duplex receptacle 20 A w/ plate | 54 | EA | 0% | 54 | n_dup
22 | 26 27 26 | Wiring devices | GFCI receptacle 20 A w/ plate | 9 | EA | 0% | 9 | n_gfci
23 | 26 27 26 | Wiring devices | Dedicated receptacle 20 A w/ plate | 4 | EA | 0% | 4 | n_ded
24 | 26 09 23 | Wiring devices | Wall-box occupancy sensor | 10 | EA | 0% | 10 | n_occw
25 | 26 09 23 | Wiring devices | Ceiling occupancy sensor + power pack | 6 | EA | 0% | 6 | n_occc
26 | 26 27 26 | Wiring devices | Toggle switch 20 A w/ plate | 2 | EA | 0% | 2 | n_sw
27 | 26 51 00 | Lighting | Type A 2x4 LED troffer 40 W | 73 | EA | 0% | 73 | fx_a
28 | 26 51 00 | Lighting | Type B 6" LED downlight 15 W | 8 | EA | 0% | 8 | fx_b
29 | 26 51 00 | Lighting | Type C 2x2 LED flat panel 30 W | 4 | EA | 0% | 4 | fx_c
30 | 26 51 00 | Lighting | Type D 4' LED strip 40 W | 3 | EA | 0% | 3 | fx_d
31 | 26 51 00 | Lighting | Type X exit / emergency combo | 6 | EA | 0% | 6 | fx_x
32 | 26 51 00 | Lighting | Fixture count check: lighting-circuit devices in schedule | 94 | EA | 0% | 94 | Σ[Circuit Schedule: Devices / fixtures where Type = "L"] | Must equal the sum of Types A-X above
33 | 26 05 00 | Equipment connections & testing | RTU / exhaust fan / WH final connections | 5 | EA | 0% | 5 | 2+2+1
34 | 26 08 00 | Equipment connections & testing | Testing, circuit directory, labeling | 1 | LS | 0% | 1 | 1 (counted / stated)

## Pricing
F&K Estimatings
Electrical Takeoff Sample — Pricing (illustrative unit costs)
Sample deliverable — prepared on a representative project to show format and level of detail. Not a client project. Quantities are computed from the sample project dimensions stated below; unit costs are illustrative (pricing basis: September 2026, national average, not a quote).
Unit costs and labor rates are illustrative, September 2026 national average; not a quote. Labor hr/unit = stated productivity. Rates are named assumptions.
Item | Group | Description | Qty incl. waste | Unit | Material $/unit | Material $ | Labor hr/unit | Labor hrs | Labor rate $/hr | Labor $ | Equip $/unit | Equip $ | Total $
1 | Distribution | Panelboard MDP 400 A MCB, 208Y/120 V 3-ph 4-W, 30 ckt (incl. breakers) | 1 | EA | 4800 | 4800 | 24 | 24 | 82 | 1968 | 0 | 0 | 6768
2 | Distribution | Panelboard LP-1 225 A MLO, 42 ckt (incl. branch breakers) | 1 | EA | 2400 | 2400 | 12 | 12 | 82 | 984 | 0 | 0 | 3384
3 | Distribution | Feeder MDP to LP-1: 2-1/2" EMT | 15.75 | LF | 7.5 | 118.125 | 0.11 | 1.7325 | 82 | 142.065 | 0 | 0 | 260.19
4 | Distribution | Feeder: 4 x 4/0 THHN Cu (3 phase + full neutral) | 92.4 | LF | 4.6 | 425.04 | 0.028 | 2.5872 | 82 | 212.1504 | 0 | 0 | 637.1904
5 | Distribution | Feeder: 1 x #4 THHN Cu equipment ground | 23.1 | LF | 1.35 | 31.185 | 0.012 | 0.2772 | 82 | 22.7304 | 0 | 0 | 53.9154
6 | Distribution | Disconnect 60 A 3-pole NEMA 3R (RTUs) | 2 | EA | 210 | 420 | 3 | 6 | 82 | 492 | 0 | 0 | 912
7 | Distribution | Disconnect 30 A 2-pole (WH-1) | 1 | EA | 95 | 95 | 2 | 2 | 82 | 164 | 0 | 0 | 259
10 | Raceway | EMT 3/4" (branch circuits) | 3570 | LF | 1.05 | 3748.5 | 0.04 | 142.8 | 82 | 11709.6 | 0 | 0 | 15458.1
11 | Raceway | EMT 1" (RTU circuits) | 132.3 | LF | 1.75 | 231.525 | 0.05 | 6.615 | 82 | 542.43 | 0 | 0 | 773.955
12 | Raceway | EMT couplings (1 per 10' stick) | 371 | EA | 0.85 | 315.35 | 0 | 0 | 82 | 0 | 0 | 0 | 315.35
13 | Raceway | EMT straps (1 per 8') | 463 | EA | 0.3 | 138.9 | 0 | 0 | 82 | 0 | 0 | 0 | 138.9
14 | Raceway | Device boxes 4" sq. w/ mud ring | 79 | EA | 3.8 | 300.2 | 0.25 | 19.75 | 82 | 1619.5 | 0 | 0 | 1919.7
15 | Raceway | Lighting j-boxes above ceiling (1 per fixture) | 94 | EA | 3.2 | 300.8 | 0.2 | 18.8 | 82 | 1541.6 | 0 | 0 | 1842.4
16 | Raceway | EMT connectors (2 per box) | 346 | EA | 0.95 | 328.7 | 0 | 0 | 82 | 0 | 0 | 0 | 328.7
17 | Wire | THHN Cu #12 (phase, neutral and ground) | 1511.4 | LF | 0.19 | 287.166 | 0.0055 | 8.3127 | 82 | 681.6414 | 0 | 0 | 968.8074
18 | Wire | THHN Cu #10 (phase, neutral and ground) | 10468.7 | LF | 0.3 | 3140.61 | 0.0065 | 68.0465 | 82 | 5579.8171 | 0 | 0 | 8720.4271
19 | Wire | THHN Cu #8 (phase, neutral and ground) | 429 | LF | 0.52 | 223.08 | 0.009 | 3.861 | 82 | 316.602 | 0 | 0 | 539.682
20 | Wire | MC fixture whips 6' (3-wire #12) | 94 | EA | 9.5 | 893 | 0.2 | 18.8 | 82 | 1541.6 | 0 | 0 | 2434.6
21 | Wiring devices | Duplex receptacle 20 A w/ plate | 54 | EA | 3.5 | 189 | 0.3 | 16.2 | 82 | 1328.4 | 0 | 0 | 1517.4
22 | Wiring devices | GFCI receptacle 20 A w/ plate | 9 | EA | 22 | 198 | 0.4 | 3.6 | 82 | 295.2 | 0 | 0 | 493.2
23 | Wiring devices | Dedicated receptacle 20 A w/ plate | 4 | EA | 4.5 | 18 | 0.3 | 1.2 | 82 | 98.4 | 0 | 0 | 116.4
24 | Wiring devices | Wall-box occupancy sensor | 10 | EA | 38 | 380 | 0.5 | 5 | 82 | 410 | 0 | 0 | 790
25 | Wiring devices | Ceiling occupancy sensor + power pack | 6 | EA | 85 | 510 | 0.8 | 4.8 | 82 | 393.6 | 0 | 0 | 903.6
26 | Wiring devices | Toggle switch 20 A w/ plate | 2 | EA | 3 | 6 | 0.3 | 0.6 | 82 | 49.2 | 0 | 0 | 55.2
27 | Lighting | Type A 2x4 LED troffer 40 W | 73 | EA | 95 | 6935 | 0.9 | 65.7 | 82 | 5387.4 | 0 | 0 | 12322.4
28 | Lighting | Type B 6" LED downlight 15 W | 8 | EA | 55 | 440 | 0.8 | 6.4 | 82 | 524.8 | 0 | 0 | 964.8
29 | Lighting | Type C 2x2 LED flat panel 30 W | 4 | EA | 70 | 280 | 0.8 | 3.2 | 82 | 262.4 | 0 | 0 | 542.4
30 | Lighting | Type D 4' LED strip 40 W | 3 | EA | 48 | 144 | 0.6 | 1.8 | 82 | 147.6 | 0 | 0 | 291.6
31 | Lighting | Type X exit / emergency combo | 6 | EA | 85 | 510 | 0.75 | 4.5 | 82 | 369 | 0 | 0 | 879
33 | Equipment connections & testing | RTU / exhaust fan / WH final connections | 5 | EA | 25 | 125 | 1.5 | 7.5 | 82 | 615 | 0 | 0 | 740
34 | Equipment connections & testing | Testing, circuit directory, labeling | 1 | LS | 150 | 150 | 16 | 16 | 82 | 1312 | 0 | 0 | 1462
|  | Direct cost totals |  |  |  | 28082.181 |  | 472.0822 |  | 38710.7363 |  | 0 | 66792.9173

## Summary
F&K Estimatings
Electrical Takeoff Sample — Summary
Sample deliverable — prepared on a representative project to show format and level of detail. Not a client project. Quantities are computed from the sample project dimensions stated below; unit costs are illustrative (pricing basis: September 2026, national average, not a quote).
Group | Line items | Material $ | Labor hrs | Labor $ | Equipment $ | Total $
Distribution | 7 | 8289.35 | 48.5969 | 3984.9458 | 0 | 12274.2958
Raceway | 7 | 5363.975 | 187.965 | 15413.13 | 0 | 20777.105
Wire | 4 | 4543.856 | 99.0202 | 8119.6605 | 0 | 12663.5165
Wiring devices | 6 | 1301 | 31.4 | 2574.8 | 0 | 3875.8
Lighting | 5 | 8309 | 81.6 | 6691.2 | 0 | 15000.2
Equipment connections & testing | 2 | 275 | 23.5 | 1927 | 0 | 2202
Direct cost subtotal |  | 28082.181 | 472.0822 | 38710.7363 | 0 | 66792.9173
Markups (percentages are stated assumptions — see Cover & Basis)
Sales tax on material (7.0% of material) |  |  |  |  | 7% | 1965.7527
Running subtotal | [5 empty] | 68758.67
Overhead (10.0% of running subtotal) |  |  |  |  | 10% | 6875.867
Running subtotal | [5 empty] | 75634.537
Profit (10.0% of running subtotal) |  |  |  |  | 10% | 7563.4537
Running subtotal | [5 empty] | 83197.9907
SAMPLE TOTAL (illustrative) | [5 empty] | 83197.9907
Cost per SF | [5 empty] | 13.8663
Sample deliverable — prepared on a representative project to show format and level of detail. Not a client project. Quantities are computed from the sample project dimensions stated below; unit costs are illustrative (pricing basis: September 2026, national average, not a quote).